## Sheet1
History Type | Number of Histories | Capacity | bytes/record | Number of Page Files | Required Space (MB)/history | Total Size (MB) | Total Size (GB)
boolean | 1 | 35040 | 9 | 77 | 0.30231 | 0.30231 | 0.00029522
enum | 1 | 35040 | 12 | 103 | 0.40387 | 0.40387 | 0.0003944
single precision numeric (32 bit) | 1 | 35040 | 12 | 103 | 0.40387 | 0.40387 | 0.0003944
double precision numeric (64 bit) | 1 | 35040 | 16 | 137 | 0.53668 | 0.53668 | 0.0005241
string | 1 | 35040 | 42 | 360 | 1.4078 | 1.4078 | 0.0013748
log history | 1 | 50000 | 72 | 879 | 3.4351 | 3.4351 | 0.0033546
audit history | 1 | 50000 | 103 | 1258 | 4.9156 | 4.9156 | 0.0048004
alarm database | 1 | 50000 | 1030 | 12574 | 49.1187 | 49.1187 | 0.047967
total | [5 empty] | 60.5239 | 0.059105
enter number of histories for each type in the station and the configured capacity to determine required file space for storing histories and alarm databases.
numeric histories by default are single precision and can be set to double precision by configuring the historyExt.
there are 35040 records per year at 15 minute interval.
250000 records is max capacity of the standard alarm database.
bytes/record are estimates for string, log history, audit history and alarm database. Actual size of records may vary and should be verified.
page files are 4096 bytes each and are added as required to store configured record capacity.
total size is projected file space required when all histories are at their full capacity.